| Date |  |  | Project/Customer | BDx_CGK4_JAH |
| --- | --- | --- | --- | --- |
| Inspector |  |  | Product Name | Containment |
|  |  | SN. Product |  |  |

| 1 | Technical Specification |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item Check |  | Detail |  |  |  | Remark |
| Dimension |  | H (……………………) × W (………………......) × D (…......…………..) mm |  |  |  |  |
| Material Type |  | SPCC / SS / Alum / Galvalum |  |  |  |  |
| Material Thickness |  | (……..…...) mm |  |  |  |  |
| Coating Type |  | Texture / Glossy / Semi Glossy |  |  |  |  |
| Color Type |  | Black Shandy |  |  |  |  |
| Rack server QTY |  |  |  |  |  |  |
|  | Visual Check |  |  |  |  |  |
| item check |  | Detail | Result |  |  | Remark |
|  |  |  | OK | NG | N/A |  |
| Dent |  | No Dents On The Panel | ⬜ | ⬜ | ⬜ |  |
| Scratch |  | No Scratch On The Panel | ⬜ | ⬜ | ⬜ |  |
| Spatter |  | No Spatter On The Panel | ⬜ | ⬜ | ⬜ |  |
| Missing Parts |  | No Missing Part | ⬜ | ⬜ | ⬜ |  |
|  |  | Installation Part Not Wrong | ⬜ | ⬜ | ⬜ |  |
| Bolt – Nut – Screw |  | According To Specification | ⬜ | ⬜ | ⬜ |  |
|  |  | Plate Washer & Spring Washer | ⬜ | ⬜ | ⬜ |  |
|  |  | Tightness | ⬜ | ⬜ | ⬜ |  |

| Function Check |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| item check | Detail | Result |  |  | Remark |
|  |  | OK | NG | N/A |  |
| Door Control Front | Open Door Front with button exit front | ⬜ | ⬜ | ⬜ |  |
|  | Open Door Front with Software Control | ⬜ | ⬜ | ⬜ |  |
|  | Cannot Close while any object between door sliding | ⬜ | ⬜ | ⬜ |  |
|  | During Close process, Auto open while any object insert between door sliding | ⬜ | ⬜ | ⬜ |  |
|  | Enable/Disable Always open Front Door with Software Control | ⬜ | ⬜ | ⬜ |  |
|  | Button Emergency for Cut OFF Power Front Door | ⬜ | ⬜ | ⬜ |  |
| Door Control Rear | Open Door Rear with button exit rear | ⬜ | ⬜ | ⬜ |  |
|  | Open Door Rear with Software Control | ⬜ | ⬜ | ⬜ |  |
|  | Cannot Close while any object between door sliding | ⬜ | ⬜ | ⬜ |  |
|  | During Close process, Auto open while any object insert between door sliding | ⬜ | ⬜ | ⬜ |  |
|  | Enable/Disable Always open Door Rear with Software Control | ⬜ | ⬜ | ⬜ |  |
|  | Button Emergency for Cut OFF Power Door Rear | ⬜ | ⬜ | ⬜ |  |
| Emergency System | The Way to Triggered Active Emergency System : |  |  |  |  |
|  | 1. Button Emergency | ⬜ | ⬜ | ⬜ |  |
|  | 2. Smoke Detector | ⬜ | ⬜ | ⬜ |  |
|  | 3. Actice Relay FSS on Box juction | ⬜ | ⬜ | ⬜ |  |
|  | 4. Temperature above value upper threshold | ⬜ | ⬜ | ⬜ |  |
|  | Containment will do this while Emergency is Activated: |  |  |  |  |
|  | 1. Auto Open Ceiilling | ⬜ | ⬜ | ⬜ |  |
|  | 2. Auto Open Front Door. and always open during emergency | ⬜ | ⬜ | ⬜ |  |
|  | 3. Auto Open Rear Door. and always open during emergency | ⬜ | ⬜ | ⬜ |  |
|  | 4. Pilot Buzzer and Lamp ON | ⬜ | ⬜ | ⬜ |  |
|  | 5. LED Light ON | ⬜ | ⬜ | ⬜ |  |
|  | Containment will do this while Emergency is De-activated: while emergency OFF/ De-activated, will be delay about 10s-15s before containtment do this: |  |  |  |  |
|  | 1. Can Close Ceiilling | ⬜ | ⬜ | ⬜ |  |
|  | 2. Auto Close Front Door. and always open during emergency | ⬜ | ⬜ | ⬜ |  |
|  | 3. Auto Close Rear Door. and always open during emergency | ⬜ | ⬜ | ⬜ |  |
|  | 4. Pilot Buzzer and Lamp OFF | ⬜ | ⬜ | ⬜ |  |
| LED System | Auto turn On while front door open | ⬜ | ⬜ | ⬜ |  |
|  | Auto turn On while any movement detection inside Containment | ⬜ | ⬜ | ⬜ |  |
|  | Keep Turn On if any movement iniside Containment | ⬜ | ⬜ | ⬜ |  |
|  | Time delay control LED can be set on Hardware Motion Sensor | ⬜ | ⬜ | ⬜ |  |
|  | Auto turn off while there is no movement and no open front door during time delay | ⬜ | ⬜ | ⬜ |  |
| Software System | Dashboard Realtime update based sensor on Containment, this is variable must be check on Dashboard Containment: |  |  |  |  |
|  | 1. Front Door Status (Open/Close) | ⬜ | ⬜ | ⬜ |  |
|  | 2. Rear Door Status (Open/Close) | ⬜ | ⬜ | ⬜ |  |
|  | 3. Ceilling Status (Open/Close) | ⬜ | ⬜ | ⬜ |  |
|  | 4, Emergency Status (ON/OFF) | ⬜ | ⬜ | ⬜ |  |
|  | 5. Emergency Button (ON/OFF) | ⬜ | ⬜ | ⬜ |  |
|  | 6. Emergency Smoke Detector (ON/OFF) | ⬜ | ⬜ | ⬜ |  |
|  | 7. Emergency FSS (ON/OFF) | ⬜ | ⬜ | ⬜ |  |
|  | 8. Emergency Temp (ON/OFF) | ⬜ | ⬜ | ⬜ |  |
|  | 9. Last Pooling SNMP (data last poolling snmp) | ⬜ | ⬜ | ⬜ |  |
|  | 10. Data All Temperature humidity Sensor Per Rack | ⬜ | ⬜ | ⬜ |  |
|  | Software can Control Containment from Display/Monitor |  |  |  |  |
|  | 1. Open Front Door | ⬜ | ⬜ | ⬜ |  |
|  | 2. Open Rear Door | ⬜ | ⬜ | ⬜ |  |
|  | 3. Enable Always Open Front Door | ⬜ | ⬜ | ⬜ |  |
|  | 4. Disable Always Open Front Door | ⬜ | ⬜ | ⬜ |  |
|  | 5. Enable Always Open Rear Door | ⬜ | ⬜ | ⬜ |  |
|  | 6. Disable Always Open Rear Door | ⬜ | ⬜ | ⬜ |  |
|  | 7. Open Ceiiling | ⬜ | ⬜ | ⬜ |  |
|  | 8. Close Ceiiling | ⬜ | ⬜ | ⬜ |  |
|  | Software User Management |  |  |  |  |
|  | 1. Register User | ⬜ | ⬜ | ⬜ |  |
|  | 2. Delete User | ⬜ | ⬜ | ⬜ |  |
|  | 3. Register Card user | ⬜ | ⬜ | ⬜ |  |
|  | 4. Delete Card User | ⬜ | ⬜ | ⬜ |  |
|  | 5. Register Finger User | ⬜ | ⬜ | ⬜ |  |
|  | 6. Delete Finger User | ⬜ | ⬜ | ⬜ |  |
|  | Software LOG Management |  |  |  |  |
|  | 1. Log Entry Containment | ⬜ | ⬜ | ⬜ |  |
|  | 2. Log Alarmt Containment | ⬜ | ⬜ | ⬜ |  |
|  | Software Setting |  |  |  |  |
|  | 1. Setting IP Containment | ⬜ | ⬜ | ⬜ |  |
|  | 2. Setting SNMP | ⬜ | ⬜ | ⬜ |  |
|  | 3. Setting Temperature Threshold | ⬜ | ⬜ | ⬜ |  |
|  | Sofware Access: |  |  |  |  |
|  | 1. Display Monitor | ⬜ | ⬜ | ⬜ |  |
|  | 2. Web UI Based IP | ⬜ | ⬜ | ⬜ |  |
| Acces Control Front | Can open Front Door with register Finger/Card | ⬜ | ⬜ | ⬜ |  |
| Acces Control Rear | Can open Rear Door with register Finger/Card | ⬜ | ⬜ | ⬜ |  |
| SNMP System | Can Read all Status by SNMP | ⬜ | ⬜ | ⬜ |  |
|  | Can Read Log entry Containment By SNMP | ⬜ | ⬜ | ⬜ |  |
|  | Can Read Log Alarm By SNMP | ⬜ | ⬜ | ⬜ |  |

|  | Notes |
| --- | --- |
|  | Legend |
|  | OK : Conform |
|  | NG : Not Good |

| Tested By, | Witness By, | Approved By, |
| --- | --- | --- |